Air Compressor

Manufacturer:	Ingersoll-Rand

Model:		242-5N

Serial Number:	30T 708491

Location:		North building, Compressor closet

References:  Ingersoll-Rand Type-30 Air Compressors Manual

Model 242

Weekly:

- Drain the compressor condensation from the filters.

- Check oil level.

- Check air inlet filter for cleanliness, clean as needed.  Replace if necessary.

- Check the dual belts for wear and tension.

- Dust the whole unit off.

- Inspect for any unusual vibrations.

- Check safety valves for proper function.

- Visually inspect for loose bolts and fittings.

Semiannually:

- Change oil.  For maximum removal of impurities the oil must be   drained while compressor is hot.  An oil change requires 1 ¾ quarts of SAE-30 non-detergent oil.

- Lubricate motor bearings.  One pump from the grease gun is sufficient.