ESD Wrist-Strap Test Log

Week of 				 Thru

|  | # Meter Readings |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Monday | # S/A | Tuesday | # S/A | Wednesday | # S/A | Thursday | # S/A | Friday | # S/A |
| ## Brent Heaton |  |  |  |  |  |  |  |  |  |  |
| Cheyney Guymon |  |  |  |  |  |  |  |  |  |  |
| Cindi Conder |  |  |  |  |  |  |  |  |  |  |
| Colleen Hall |  |  |  |  |  |  |  |  |  |  |
| Eric Olson |  |  |  |  |  |  |  |  |  |  |
| Jason Grace |  |  |  |  |  |  |  |  |  |  |
| Jayne Wilson |  |  |  |  |  |  |  |  |  |  |
| Keith Driskill |  |  |  |  |  |  |  |  |  |  |
| Noreen Iverson |  |  |  |  |  |  |  |  |  |  |
| Raul Castillo |  |  |  |  |  |  |  |  |  |  |
| Ron Bernau |  |  |  |  |  |  |  |  |  |  |
| Ron Harris |  |  |  |  |  |  |  |  |  |  |
| Scott McIlrath |  |  |  |  |  |  |  |  |  |  |
| Scott Montgomery |  |  |  |  |  |  |  |  |  |  |
| ## Sean Childs |  |  |  |  |  |  |  |  |  |  |
| Sonja Davis |  |  |  |  |  |  |  |  |  |  |
| Stores #1 |  |  |  |  |  |  |  |  |  |  |
| Stores #2 |  |  |  |  |  |  |  |  |  |  |
| Thomi Barker |  |  |  |  |  |  |  |  |  |  |

1.  Check wrist strap at least once a week.

2.  Set meter for DC volts.

3.  Workstations:  Connect banana lead of tester to ground at wall plug/power strip.

S/A (stand alone):  Connect wrist cord banana lead to banana lead of tester.

Put a check in the “stand alone” column next to your reading.

### Limits

|  | High Limit | Low Limit |
| --- | --- | --- |
| Workstation | 0.376 | 0.095 |
| Stand-alone | 0.738 | 0.19 |

Readings below low limit:  Use lotion, tighten strap, clean skin contact plate

(if reading does not improve replace ESD strap and possibly wrist band)

Readings above high limit:  Probable static system failure; Check for broken wires

(if failure is not due to test equipment, replace ESD strap)